## Лист1
OID | Name | Type | Access | Description
.1.3.6.1.4.1.52964.1.1.1.1.0 | fwVersion | OCTET STRING | read-only | Firmware version
.1.3.6.1.4.1.52964.1.1.1.2.0 | hwRevision | OCTET STRING | read-only | Hardmware revision
.1.3.6.1.4.1.52964.1.1.1.3.0 | controllerName | OCTET STRING | read-only | Controller name
.1.3.6.1.4.1.52964.1.1.1.4.0 | hitSensor | INTEGER | read-only | Internal hit sensor state: 0 - no hit; 1 - hit detected
.1.3.6.1.4.1.52964.1.1.1.5.0 | internalTemp | INTEGER | read-only | Internal temperature in celcius
.1.3.6.1.4.1.52964.1.1.1.6.0 | status | INTEGER | read-only | Сontroller status: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.1.7.0 | alarm | INTEGER | read-only | Alarm status: 0 - alarm disabled; 1 - alarm enabled
.1.3.6.1.4.1.52964.1.1.1.8.0 | currentTime | OCTET STRING | read-only | CurrentTime
.1.3.6.1.4.1.52964.1.1.1.9.0 | guard | INTEGER | read-write | Guard system status: 0 - guard not changed; 1 - toggle status
.1.3.6.1.4.1.52964.1.1.1.10.0 | restore | INTEGER | read-write | Settings restore: 0 - normal state; 1 - restore
.1.3.6.1.4.1.52964.1.1.1.11.0 | reboot | INTEGER | read-write | System reboot status: 0 - normal state; 1 - reboot
.1.3.6.1.4.1.52964.1.1.2.1.1.(1..12) | dinIndex | INTEGER | read-only | Digital input index: 1..12
.1.3.6.1.4.1.52964.1.1.2.1.2.(1..12) | dinName | OCTET STRING | read-write | Digital input name
.1.3.6.1.4.1.52964.1.1.2.1.3.(1..12) | dinState | INTEGER | read-only | Digital input state: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.2.1.4.(1..12) | dinValue | INTEGER | read-only | Digital input value: 1.For DIN template "Impulse counter": impulse count 2.For DIN template "RS-HT1": - bit0..15 - temperature *10 ᵒC; - bit16..31 - humidity *10 %RH. Example: dinValue = 0x00E0 00FD Temperature = 0x00FD/10 = 253/10 = 25,3 ᵒC Humidity = 0x00E0/10 = 224/10 = 22,4 %RH 3.For another templates: state on DIN pin (0/1)
.1.3.6.1.4.1.52964.1.1.3.1.1.(1..4) | ainIndex | INTEGER | read-only | Analog input index: 1..4
.1.3.6.1.4.1.52964.1.1.3.1.2.(1..4) | ainName | OCTET STRING | read-write | Analog input name
.1.3.6.1.4.1.52964.1.1.3.1.3.(1..4) | ainState | INTEGER | read-only | Analog input state: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.3.1.4.(1..4) | ainValue | INTEGER | read-only | Input current (mA)
.1.3.6.1.4.1.52964.1.1.4.1.1.(1..42) | socketIndex | INTEGER | read-only | Socket index: 1..42
.1.3.6.1.4.1.52964.1.1.4.1.2.(1..42) | socketLocation | INTEGER | read-only | Socket location: 0 - PDU;
.1.3.6.1.4.1.52964.1.1.4.1.3.(1..42) | socketName | OCTET STRING | read-write | Socket name
.1.3.6.1.4.1.52964.1.1.4.1.4.(1..42) | socketState | INTEGER | read-write | Socket state: 0 - off; 1 - on
.1.3.6.1.4.1.52964.1.1.4.1.5.(1..42) | socketVoltage | INTEGER | read-only | Socket Voltage [0.01V]
.1.3.6.1.4.1.52964.1.1.4.1.6.(1..42) | socketCurrent | INTEGER | read-only | Socket Current [0.01A]
.1.3.6.1.4.1.52964.1.1.4.1.7.(1..42) | socketPower | INTEGER | read-only | Socket Power [0.1kW]
.1.3.6.1.4.1.52964.1.1.4.1.8.(1..42) | socketEnergy | INTEGER | read-only | Socket active energy [0.01 kWh] A negative value indicates that the energy value is unavailable
.1.3.6.1.4.1.52964.1.1.5.1.1.(1..12) | conditionIndex | INTEGER | read-only | Condition index: 1..12
.1.3.6.1.4.1.52964.1.1.5.1.2.(1..12) | conditionName | OCTET STRING | read-write | Condition name
.1.3.6.1.4.1.52964.1.1.5.1.3.(1..12) | conditionState | INTEGER | read-only | Condition state: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.5.1.4.(1..12) | conditionAddr | INTEGER | read-write | Condition address
.1.3.6.1.4.1.52964.1.1.5.1.5.(1..12) | conditionModel | INTEGER | read-only | Condition model: 0 - Condition REM; 1 - Condition REM-5U
.1.3.6.1.4.1.52964.1.1.5.1.6.(1..12) | conditionStatus | INTEGER | read-only | Condition unit REM status Bit field 'abcd', where a - Is heater running; b - Is compressor running; c - Is external fan running; d - Is internal fan running.
.1.3.6.1.4.1.52964.1.1.5.1.7.(1..12) | conditionError | INTEGER | read-only | Condition unit error code
.1.3.6.1.4.1.52964.1.1.5.1.8.(1..12) | coolingTurnOffPoint | INTEGER | read-write | Condition cooling turn off point
.1.3.6.1.4.1.52964.1.1.5.1.9.(1..12) | coolingHysteresis | INTEGER | read-write | Condition cooling hysteresis
.1.3.6.1.4.1.52964.1.1.5.1.10.(1..12) | heatingTurnOffPoint | INTEGER | read-write | Condition heating turn off point
.1.3.6.1.4.1.52964.1.1.5.1.11.(1..12) | heatingHysteresis | INTEGER | read-write | Condition heating hysteresis
.1.3.6.1.4.1.52964.1.1.5.1.12.(1..12) | fanTurnOffPoint | INTEGER | read-write | Condition internal fan turn off temperature
.1.3.6.1.4.1.52964.1.1.5.1.13.(1..12) | evaporatorTemp | INTEGER | read-only | Current condition evaporator temperature
.1.3.6.1.4.1.52964.1.1.5.1.14.(1..12) | condenserTemp | INTEGER | read-only | Current condition condenser temperature
.1.3.6.1.4.1.52964.1.1.5.1.15.(1..12) | indoorTemp | INTEGER | read-only | Current condition indoor temperature
.1.3.6.1.4.1.52964.1.1.5.1.16.(1..12) | onOff | INTEGER | read-write | Condition unit on/off command: 0 - off; 1 - on
.1.3.6.1.4.1.52964.1.1.5.1.17.(1..12) | temperatureSetPoint | INTEGER | read-write | Condition unit temperature set point
.1.3.6.1.4.1.52964.1.1.5.1.18.(1..12) | temperatureSensitivitySetPoint | INTEGER | read-write | Condition unit temperature sensitivity set point
.1.3.6.1.4.1.52964.1.1.5.1.19.(1..12) | humiditySetPoint | INTEGER | read-write | Condition unit humidity set point
.1.3.6.1.4.1.52964.1.1.5.1.20.(1..12) | humiditySensitivitySetPoint | INTEGER | read-write | Condition unit humidity sensitivity set point
.1.3.6.1.4.1.52964.1.1.5.1.21.(1..12) | highTemperatureSetPoint | INTEGER | read-write | Condition unit high temperature set point
.1.3.6.1.4.1.52964.1.1.5.1.22.(1..12) | lowTemperatureSetPoint | INTEGER | read-write | Condition unit low temperature set point
.1.3.6.1.4.1.52964.1.1.5.1.23.(1..12) | highHumiditySetPoint | INTEGER | read-write | Condition unit high humidity set point
.1.3.6.1.4.1.52964.1.1.5.1.24.(1..12) | lowHumiditySetPoint | INTEGER | read-write | Condition unit low humidity set point
.1.3.6.1.4.1.52964.1.1.5.1.25.(1..12) | returnAirTemperature | INTEGER | read-only | Condition unit return air temperature
.1.3.6.1.4.1.52964.1.1.5.1.26.(1..12) | supplyAirTemperature | INTEGER | read-only | Condition unit supply air temperature
.1.3.6.1.4.1.52964.1.1.5.1.27.(1..12) | returnAirHumidity | INTEGER | read-only | Condition unit return air humidity
.1.3.6.1.4.1.52964.1.1.6.1.1.(1..4) | energyMeterIndex | INTEGER | read-only | Energy meter index: 1..4
.1.3.6.1.4.1.52964.1.1.6.1.2.(1..4) | energyMeterName | OCTET STRING | read-write | Energy meter name
.1.3.6.1.4.1.52964.1.1.6.1.3.(1..4) | energyMeterState | INTEGER | read-only | Energy meter state: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.6.1.4.(1..4) | energyMeterId | OCTET STRING | read-write | Energy meter address
.1.3.6.1.4.1.52964.1.1.6.1.5.(1..4) | energyMeterModel | INTEGER | read-only | Energy meter model
.1.3.6.1.4.1.52964.1.1.6.1.6.(1..4) | totalPower | INTEGER | read-only | Energy meter total power consumed
.1.3.6.1.4.1.52964.1.1.6.1.7.(1..4) | totalT1Power | INTEGER | read-only | Energy meter tariff 1 total power consumed
.1.3.6.1.4.1.52964.1.1.6.1.8.(1..4) | totalT2Power | INTEGER | read-only | Energy meter tariff 2 total power consumed
.1.3.6.1.4.1.52964.1.1.6.1.9.(1..4) | totalT3Power | INTEGER | read-only | Energy meter tariff 3 total power consumed
.1.3.6.1.4.1.52964.1.1.6.1.10.(1..4) | voltsPhase1 | INTEGER | read-only | Energy meter phase 1 voltage
.1.3.6.1.4.1.52964.1.1.6.1.11.(1..4) | voltsPhase2 | INTEGER | read-only | Energy meter phase 2 voltage
.1.3.6.1.4.1.52964.1.1.6.1.12.(1..4) | voltsPhase3 | INTEGER | read-only | Energy meter phase 3 voltage
.1.3.6.1.4.1.52964.1.1.6.1.13.(1..4) | currentPhase1 | INTEGER | read-only | Energy meter phase 1 current
.1.3.6.1.4.1.52964.1.1.6.1.14.(1..4) | currentPhase2 | INTEGER | read-only | Energy meter phase 2 current
.1.3.6.1.4.1.52964.1.1.6.1.15.(1..4) | currentPhase3 | INTEGER | read-only | Energy meter phase 3 current
.1.3.6.1.4.1.52964.1.1.6.1.16.(1..4) | wattage | INTEGER | read-only | Energy meter current total wattage
.1.3.6.1.4.1.52964.1.1.6.1.17.(1..4) | wattagePhase1 | INTEGER | read-only | Energy meter phase 1 current wattage
.1.3.6.1.4.1.52964.1.1.6.1.18.(1..4) | wattagePhase2 | INTEGER | read-only | Energy meter phase 2 current wattage
.1.3.6.1.4.1.52964.1.1.6.1.19.(1..4) | wattagePhase3 | INTEGER | read-only | Energy meter phase 3 current wattage
.1.3.6.1.4.1.52964.1.1.7.1.1.(1..12) | extTemperatureIndex | INTEGER | read-only | External temperature sensor index: 1..12
.1.3.6.1.4.1.52964.1.1.7.1.2.(1..12) | extTemperatureName | OCTET STRING | read-write | External temperature sensor name
.1.3.6.1.4.1.52964.1.1.7.1.3.(1..12) | extTemperatureState | INTEGER | read-only | External temperature sensor state: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.7.1.4.(1..10) | extTemperatureValue | INTEGER | read-only | External temperature sensor current temperature.[0.1ᵒC]
.1.3.6.1.4.1.52964.1.1.8.1.1.(1..12) | thermocontrollerIndex | INTEGER | read-only | Thermocontroller index: 1..12
.1.3.6.1.4.1.52964.1.1.8.1.2.(1..12) | thermocontrollerName | OCTET STRING | read-write | Thermocontroller name
.1.3.6.1.4.1.52964.1.1.8.1.3.(1..12) | thermocontrollerState | INTEGER | read-only | Thermocontroller state: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.8.1.4.(1..12) | remDMTHIndoorTempValue | INTEGER | read-only | R-MC-DMTH indoor temperature value [0.1deg.C]
.1.3.6.1.4.1.52964.1.1.8.1.5.(1..12) | remDMTHIndoorHumidValue | INTEGER | read-only | R-MC-DMTH indoor humidity value [0.1%RH]
.1.3.6.1.4.1.52964.1.1.8.1.6.(1..12) | remDMTHOutdoorTempValue | INTEGER | read-only | R-MC-DMTH outdoor temperature sensor value [0.1deg.C]
.1.3.6.1.4.1.52964.1.1.8.1.7.(1..12) | remDMTHT1TempValue | INTEGER | read-only | R-MC-DMTH temperature sensor T1 value [0.1deg.C]
.1.3.6.1.4.1.52964.1.1.8.1.8.(1..12) | remDMTHT1State | INTEGER | read-only | R-MC-DMTH temperature sensor T1 state: 0 - Error; 1 - Normal
.1.3.6.1.4.1.52964.1.1.8.1.9.(1..12) | remDMTHT2TempValue | INTEGER | read-only | R-MC-DMTH temperature sensor T2 value [0.1deg.C]
.1.3.6.1.4.1.52964.1.1.8.1.10.(1..12) | remDMTHT2State | INTEGER | read-only | R-MC-DMTH temperature sensor T2 state: 0 - Error; 1 - Normal
.1.3.6.1.4.1.52964.1.1.8.1.11.(1..12) | remDMTHTHTempValue | INTEGER | read-only | R-MC-DMTH temperature sensor TH value [0.1deg.C]
.1.3.6.1.4.1.52964.1.1.8.1.12.(1..12) | remDMTHTHState | INTEGER | read-only | R-MC-DMTH temperature sensor TH state: 0 - Error; 1 - Normal
.1.3.6.1.4.1.52964.1.1.8.1.13.(1..12) | remDMTHRelayActiveState | INTEGER | read-only | R-MC-DMTH active equipment relay state: 0 - Off; 1 - On
.1.3.6.1.4.1.52964.1.1.8.1.14.(1..12) | remDMTHRelayFanState | INTEGER | read-only | R-MC-DMTH fan relay state: 0 - Off; 1 - On
.1.3.6.1.4.1.52964.1.1.8.1.15.(1..12) | remDMTHRelayHeatState | INTEGER | read-only | R-MC-DMTH heat relay state: 0 - Off; 1 - On
.1.3.6.1.4.1.52964.1.1.8.1.16.(1..12) | remDMTHAlarm | INTEGER | read-only | R-MC-DMTH alarms mask: bit 0 - Alarm mode; bit 1 - Overheat; bit 2 - Cold start; bit 5 - Heat alarm; bit 6 - Sensor T1 alarm; bit 7 - Sensor T2 alarm; bit 8 - Sensor TH alarm; bit 11 - Reserve sensor alarm; bit 12 - Outdoor sensor alarm; bit 13 - Humidity sensor alarm; bit 14 - Low temperature; bit 15 - Hi temperature; bit 16 - Hi humidity; bit 18 - Low temperature protection; bit 19 - Hi humidity protection
.1.3.6.1.4.1.52964.1.1.9.1.1.(1..6) | rsht1Index | INTEGER | read-only | RS-HT1 index: 1..6
.1.3.6.1.4.1.52964.1.1.9.1.2.(1..6) | rsht1DinIdx | INTEGER | read-only | RS-HT1 connected DIN Index
.1.3.6.1.4.1.52964.1.1.9.1.3.(1..6) | rsht1Name | OCTET STRING | read-write | RS-HT1 name
.1.3.6.1.4.1.52964.1.1.9.1.4.(1..6) | rsht1HighTempAlmaj | INTEGER | read-write | RS-HT1 high temperature alarm major level.[0.1ᵒC]
.1.3.6.1.4.1.52964.1.1.9.1.5.(1..6) | rsht1HighTempAlmim | INTEGER | read-write | RS-HT1 high temperature alarm minor level.[0.1ᵒC]
.1.3.6.1.4.1.52964.1.1.9.1.6.(1..6) | rsht1LowTempAlmaj | INTEGER | read-write | RS-HT1 low temperature alarm major level.[0.1ᵒC]
.1.3.6.1.4.1.52964.1.1.9.1.7.(1..6) | rsht1LowTempAlmim | INTEGER | read-write | RS-HT1 low temperature alarm minor level.[0.1ᵒC]
.1.3.6.1.4.1.52964.1.1.9.1.8.(1..6) | rsht1HighHumidAlmaj | INTEGER | read-write | RS-HT1 high humidity alarm major level.[0.1%RH]
.1.3.6.1.4.1.52964.1.1.9.1.9.(1..6) | rsht1HighHumidAlmim | INTEGER | read-write | RS-HT1 high humidity alarm minor level.[0.1%RH]
.1.3.6.1.4.1.52964.1.1.9.1.10.(1..6) | rsht1LowHumidAlmaj | INTEGER | read-write | RS-HT1 low humidity alarm major level.[0.1%RH]
.1.3.6.1.4.1.52964.1.1.9.1.11.(1..6) | rsht1LowHumidAlmim | INTEGER | read-write | RS-HT1 low humidity alarm minor level.[0.1%RH]
.1.3.6.1.4.1.52964.1.1.9.1.12.(1..6) | rsht1State | INTEGER | read-only | RS-HT1 state: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.9.1.13.(1..6) | rsht1TempValue | INTEGER | read-only | RS-HT1 current temperature.[0.1ᵒC]
.1.3.6.1.4.1.52964.1.1.9.1.14.(1..6) | rsht1HumidValue | INTEGER | read-only | RS-HT1 сurrent humidity.[0.1%RH]
.1.3.6.1.4.1.52964.1.1.9.1.15.(1..6) | rsht1DataTimestamp | Unsigned32 | read-only | Time of the last successful data read in Unix epochs
.1.3.6.1.4.1.52964.1.1.10.1.0 | pduPowerPhaseAVoltage | INTEGER | read-only | Input monitoring phase A Voltage. [0.01V]
.1.3.6.1.4.1.52964.1.1.10.2.0 | pduPowerPhaseBVoltage | INTEGER | read-only | Input monitoring phase B Voltage. [0.01V]
.1.3.6.1.4.1.52964.1.1.10.3.0 | pduPowerPhaseCVoltage | INTEGER | read-only | Input monitoring phase C Voltage. [0.01V]
.1.3.6.1.4.1.52964.1.1.10.4.0 | pduPowerPhaseACurrent | INTEGER | read-only | Input monitoring phase A Current. [0.01A]
.1.3.6.1.4.1.52964.1.1.10.5.0 | pduPowerPhaseBCurrent | INTEGER | read-only | Input monitoring phase B Current. [0.01A]
.1.3.6.1.4.1.52964.1.1.10.6.0 | pduPowerPhaseCCurrent | INTEGER | read-only | Input monitoring phase C Current. [0.01A]
.1.3.6.1.4.1.52964.1.1.10.7.0 | pduPowerPhaseAActivePower | INTEGER | read-only | Input monitoring phase A Active Power. [0.1kW]
.1.3.6.1.4.1.52964.1.1.10.8.0 | pduPowerPhaseBActivePower | INTEGER | read-only | Input monitoring phase B Active Power. [0.1kW]
.1.3.6.1.4.1.52964.1.1.10.9.0 | pduPowerPhaseActivePower | INTEGER | read-only | Input monitoring phase C Active Power. [0.1kW]
.1.3.6.1.4.1.52964.1.1.10.10.0 | pduPowerPhaseAReactivePower | INTEGER | read-only | Input monitoring phase A Reactive Power. [0.1kW]
.1.3.6.1.4.1.52964.1.1.10.11.0 | pduPowerPhaseBReactivePower | INTEGER | read-only | Input monitoring phase B Reactive Power. [0.1kW]
.1.3.6.1.4.1.52964.1.1.10.12.0 | pduPowerPhaseCReactivePower | INTEGER | read-only | Input monitoring phase C Reactive Power. [0.1kW]
.1.3.6.1.4.1.52964.1.1.10.13.0 | pduPowerPhaseAApparentPower | INTEGER | read-only | Input monitoring phase A Apparent Power. Square root of the sum of the squares of the active and the reactive powers of the same phase. [0.1kW]
.1.3.6.1.4.1.52964.1.1.10.14.0 | pduPowerPhaseBApparentPower | INTEGER | read-only | Input monitoring phase B Apparent Power. Square root of the sum of the squares of the active and the reactive powers of the same phase. [0.1kW]
.1.3.6.1.4.1.52964.1.1.10.15.0 | pduPowerPhaseCApparentPower | INTEGER | read-only | Input monitoring phase C Apparent Power. Square root of the sum of the squares of the active and the reactive powers of the same phase. [0.1kW]
.1.3.6.1.4.1.52964.1.1.10.16.0 | pduPowerTotalActivePower | INTEGER | read-only | Input monitoring total Active Power. [kW]
.1.3.6.1.4.1.52964.1.1.10.17.0 | pduPowerTotalReactivePower | INTEGER | read-only | Input monitoring total Reactive Power. [kW]
.1.3.6.1.4.1.52964.1.1.10.18.0 | pduPowerTotalApparentPower | INTEGER | read-only | Input monitoring total Apparent Power. [kW]
.1.3.6.1.4.1.52964.1.1.10.19.0 | pduPowerPhaseAActiveEnergy | INTEGER | read-only | Phase A active energy. [0.01 kWh] A negative value indicates that the energy value is unavailable
.1.3.6.1.4.1.52964.1.1.10.20.0 | pduPowerPhaseBActiveEnergy | INTEGER | read-only | Phase B active energy. [0.01 kWh] A negative value indicates that the energy value is unavailable
.1.3.6.1.4.1.52964.1.1.10.21.0 | pduPowerPhaseCActiveEnergy | INTEGER | read-only | Phase C active energy. [0.01 kWh] A negative value indicates that the energy value is unavailable
.1.3.6.1.4.1.52964.1.1.10.22.0 | pduPowerTotalActiveEnergy | INTEGER | read-only | Total active energy. [0.01 kWh] A negative value indicates that the energy value is unavailable
.1.3.6.1.4.1.52964.1.1.11.1.1.(1..12) | remLockIndex | INTEGER | read-only | REM-Lock index: 1..12
.1.3.6.1.4.1.52964.1.1.11.1.2.(1..12) | remLockName | OCTET STRING | read-write | REM-Lock name
.1.3.6.1.4.1.52964.1.1.11.1.3.(1..12) | remLockState | INTEGER | read-only | REM-Lock handle state: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.11.1.4.(1..12) | remLockStatus | INTEGER | read-only | REM-Lock handle status: 0 - not connected 1 - Blocked 2 - Unblocked 3 - Open
.1.3.6.1.4.1.52964.1.1.11.1.5.(1..12) | remLockOpen | INTEGER | read-write | REM-Lock handle lock status: 0 - Blocked 1 - Unblocked
.1.3.6.1.4.1.52964.1.1.11.1.6.(1..12) | remLockLastSwipedCardID | Unsigned32 | read-only | REM-Lock last swiped card ID
.1.3.6.1.4.1.52964.1.1.11.1.8.(1..12) | remLockLastSwipedCardType | INTEGER | read-only | REM-Lock last swiped card type: 0 - unknown 1 - Mifare Classic 2 - Mifare Plus 3 - EM marine 4 - HID prox
.1.3.6.1.4.1.52964.1.1.11.1.9.(1..12) | remLockLastSwipedCardTime | Unsigned32 | read-only | REM-Lock last swipe card timestamp in Unix epochs
.1.3.6.1.4.1.52964.1.1.11.1.10.(1..12) | remLockLastSwipedCardSuccess | INTEGER | read-only | REM-Lock last swipe card success 0 - unsuccessful attempt to pass 1 - successful pass
.1.3.6.1.4.1.52964.1.1.11.1.11.(1..12) | remLockLastUnlockTimestamp | Unsigned32 | read-only | REM-Lock last unlcock timestamp in Unix epochs
.1.3.6.1.4.1.52964.1.1.11.1.12.(1..12) | remLockDataTimestamp | Unsigned32 | read-only | REM-Lock data timestamp in Unix epochs
.1.3.6.1.4.1.52964.1.1.12.1.1.(1..12) | extAtsIndex | INTEGER | read-only | External ATS device index: 1..12
.1.3.6.1.4.1.52964.1.1.12.1.2.(1..12) | extAtsName | OCTET STRING | read-write | External ATS device name
.1.3.6.1.4.1.52964.1.1.12.1.3.(1..12) | extAtsStatus | INTEGER | read-only | External ATS device status: 0 - Normal 1 - Alarm Min 2 - Alarm Maj
.1.3.6.1.4.1.52964.1.1.12.1.4.(1..12) | extAtsActiveLine | INTEGER | read-only | External ATS device active line: 0 - not connected 1 - Power from line A 2 - Power from line B
.1.3.6.1.4.1.52964.1.1.12.1.5.(1..12) | extAtsLineAVoltage | INTEGER | read-only | External ATS device line A voltage [V]
.1.3.6.1.4.1.52964.1.1.12.1.6.(1..12) | extAtsLineBVoltage | INTEGER | read-only | External ATS device line B voltage [V]
.1.3.6.1.4.1.52964.1.1.12.1.7.(1..12) | extAtsCurrent | INTEGER | read-only | External ATS device output current [0.01 A]
.1.3.6.1.4.1.52964.1.1.12.1.8.(1..12) | extAtsTotalPower | INTEGER | read-only | External ATS device output total power [W]
.1.3.6.1.4.1.52964.1.1.12.1.9.(1..12) | extAtsLineAFreq | INTEGER | read-only | External ATS device line A frequency [0.01 Hz]
.1.3.6.1.4.1.52964.1.1.12.1.10.(1..12) | extAtsLineBFreq | INTEGER | read-only | External ATS device line B frequency [0.01 Hz]
.1.3.6.1.4.1.52964.1.1.12.1.11.(1..12) | extAtsAlarmFlags | INTEGER | read-only | External ATS device alarm flags
.1.3.6.1.4.1.52964.1.1.13.1.1.(1..12) | remFloodIndex | INTEGER | read-only | REM-Flood index
.1.3.6.1.4.1.52964.1.1.13.1.2.(1..12) | remFloodName | OCTET STRING | read-write | REM-Flood name
.1.3.6.1.4.1.52964.1.1.13.1.3.(1..12) | remFloodStatus | INTEGER | read-only | REM-Flood status: 0 - Normal 1 - Alarm Min 2 - Alarm Maj
.1.3.6.1.4.1.52964.1.1.13.1.4.(1..12) | remFloodState | INTEGER | read-only | REM-Flood state: 0 - Not flooded 1 - Flooded
.1.3.6.1.4.1.52964.1.1.20.1.1.(1..6) | pduBankIndex | INTEGER | read-only | PDU Bank index: 1..6
.1.3.6.1.4.1.52964.1.1.20.1.2.(1..6) | pduBankName | OCTET STRING | read-write | PDU Bank Name
.1.3.6.1.4.1.52964.1.1.20.1.3.(1..6) | pduBankState | INTEGER | read-only | PDU Bank State: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.20.1.4.(1..6) | pduBankVoltage | INTEGER | read-only | PDU Bank Voltage [0.01V]
.1.3.6.1.4.1.52964.1.1.20.1.5.(1..6) | pduBankCurrent | INTEGER | read-only | PDU Bank Current [0.01A]
.1.3.6.1.4.1.52964.1.1.20.1.6.(1..6) | pduBankPower | INTEGER | read-only | PDU Bank active power [0.1kW]
.1.3.6.1.4.1.52964.1.1.20.1.7.(1..6) | pduBankActiveEnergy | INTEGER | read-only | PDU Bank active energy [0.01 kWh] A negative value indicates that the energy value is unavailable
.1.3.6.1.4.1.52964.1.1.20.1.8.(1..6) | pduBankReactiveEnergy | INTEGER | read-only | PDU Bank reactive energy [0.01 kVARh] A negative value indicates that the energy value is unavailable
.1.3.6.1.4.1.52964.1.1.20.1.9.(1..6) | pduBankApparentEnergy | INTEGER | read-only | PDU Bank active energy [0.01 kVAh] A negative value indicates that the energy value is unavailable
.1.3.6.1.4.1.52964.1.1.20.1.10.(1..6) | pduBankReactivePower | INTEGER | read-only | PDU Bank reactive power [0.1kVAR]
.1.3.6.1.4.1.52964.1.1.20.1.11.(1..6) | pduBankApparentPower | INTEGER | read-only | PDU Bank apparent power [0.1kVA]
.1.3.6.1.4.1.52964.1.1.21.1.1.(1..3) | pduPhaseIndex | INTEGER | read-only | PDU Phase index: 1..6
.1.3.6.1.4.1.52964.1.1.21.1.2.(1..3) | pduPhaseName | OCTET STRING | read-only | PDU Phase Name
.1.3.6.1.4.1.52964.1.1.21.1.3.(1..3) | pduPhaseState | INTEGER | read-only | PDU Phase State: 0 - Normal; 1 - Alarm Minor; 2 - Alarm Major
.1.3.6.1.4.1.52964.1.1.21.1.4.(1..3) | pduPhaseVoltage | INTEGER | read-only | PDU Phase Voltage [0.01V]
.1.3.6.1.4.1.52964.1.1.21.1.5.(1..3) | pduPhaseCurrent | INTEGER | read-only | PDU Phase Current [0.01A]
.1.3.6.1.4.1.52964.1.1.21.1.6.(1..3) | pduPhaseActivePower | INTEGER | read-only | PDU Phase Active Power [0.1kW]
.1.3.6.1.4.1.52964.1.1.21.1.7.(1..3) | pduPhaseReactivePower | INTEGER | read-only | PDU Phase Reactive Power [0.1kVAR]
.1.3.6.1.4.1.52964.1.1.21.1.8.(1..3) | pduPhaseApparentPower | INTEGER | read-only | PDU Phase Apparent Power [0.1kVA]
.1.3.6.1.4.1.52964.1.1.21.1.9.(1..3) | pduPhaseActiveEnergy | INTEGER | read-only | PDU Phase Active Energy [0.01kWh]
.1.3.6.1.4.1.52964.1.1.21.1.10.(1..3) | pduPhaseReactiveEnergy | INTEGER | read-only | PDU Phase Reactive Energy [0.01kVARh]
.1.3.6.1.4.1.52964.1.1.21.1.11.(1..3) | pduPhaseApparentEnergy | INTEGER | read-only | PDU Phase Apparent Energy [0.01kVAh]
.1.3.6.1.4.1.52964.1.1.30.1.0 | AtsStatus | INTEGER | read-only | ATS status: 0 - Normal 1 - Alarm Min 2 - Alarm Maj
.1.3.6.1.4.1.52964.1.1.30.2.0 | AtsActiveLine | INTEGER | read-only | ATS active line: 0 - not connected 1 - Power from line A 2 - Power from line B
.1.3.6.1.4.1.52964.1.1.30.3.0 | AtsLineAvoltage | INTEGER | read-only | ATS voltage on line A [V]
.1.3.6.1.4.1.52964.1.1.30.4.0 | AtsLineBvoltage | INTEGER | read-only | ATS voltage on line B [V]
.1.3.6.1.4.1.52964.1.1.30.5.0 | AtsLineAfrequency | INTEGER | read-only | ATS frequency on line A [0.01 Hz]
.1.3.6.1.4.1.52964.1.1.30.6.0 | AtsLineBfrequency | INTEGER | read-only | ATS frequency on line B [0.01 Hz]
.1.3.6.1.4.1.52964.1.1.30.7.0 | AtsAlarmFlags | INTEGER | read-only | ATS alarm flags
.1.3.6.1.4.1.52964.1.1.30.8.0 | AtsOutputCurrent | INTEGER | read-only | ATS output current [0.01 A]
.1.3.6.1.4.1.52964.1.1.30.9.0 | AtsOutputActivePower | INTEGER | read-only | ATS output active power [W]
.1.3.6.1.4.1.52964.1.1.50.1.1.1.(1..4) | cpduIndex | INTEGER | read-only | CPDU index: 1..4
.1.3.6.1.4.1.52964.1.1.50.1.1.2.(1..4) | cpduName | OCTET STRING | read-write | CPDU Name
.1.3.6.1.4.1.52964.1.1.50.1.1.3.(1..4) | cpduState | INTEGER | read-only | CPDU State
.1.3.6.1.4.1.52964.1.1.50.1.1.4.(1..4) | cpduModel | OCTET STRING | read-only | CPDU Model
.1.3.6.1.4.1.52964.1.1.50.1.1.5.(1..4) | cpduSerial | INTEGER | read-only | CPDU Serial A negative value means that CPDU serial number is unavailable
.1.3.6.1.4.1.52964.1.1.50.2.1.1.(1..4).(1..3) | cpduIndexPhases | INTEGER | read-only | CPDU Index: 1..4
.1.3.6.1.4.1.52964.1.1.50.2.1.2.(1..4).(1..3) | cpduPhaseIndex | INTEGER | read-only | CPDU Phase Index: 1..3
.1.3.6.1.4.1.52964.1.1.50.2.1.3.(1..4).(1..3) | cpduPhaseName | OCTET STRING | read-only | CPDU Phase Name
.1.3.6.1.4.1.52964.1.1.50.2.1.4.(1..4).(1..3) | cpduPhaseState | INTEGER | read-only | CPDU Phase State: 0 - Normal 1 - Alarm Min 2 - Alarm Maj
.1.3.6.1.4.1.52964.1.1.50.2.1.5.(1..4).(1..3) | cpduPhaseVoltage | INTEGER | read-only | CPDU Phase voltage [0.01V]
.1.3.6.1.4.1.52964.1.1.50.2.1.6.(1..4).(1..3) | cpduPhaseCurrent | INTEGER | read-only | CPDU Phase current [0.01A]
.1.3.6.1.4.1.52964.1.1.50.2.1.7.(1..4).(1..3) | cpduPhaseActivePower | INTEGER | read-only | CPDU Phase active power [0.1kW]
.1.3.6.1.4.1.52964.1.1.50.2.1.8.(1..4).(1..3) | cpduPhaseReactivePower | INTEGER | read-only | CPDU Phase reactive power [0.1kVAR] A negative value indicates that the measure value is unavailable.
.1.3.6.1.4.1.52964.1.1.50.2.1.9.(1..4).(1..3) | cpduPhaseApparentPower | INTEGER | read-only | CPDU Phase apparent power [0.1kVA] A negative value indicates that the measure value is unavailable.
.1.3.6.1.4.1.52964.1.1.50.2.1.10.(1..4).(1..3) | cpduPhaseActiveEnergy | INTEGER | read-only | CPDU Phase active energy [0.01 kWh] A negative value indicates that the energy value is unavailable.
.1.3.6.1.4.1.52964.1.1.50.3.1.1.(1..4).(1..6) | cpduIndexBanks | INTEGER | read-only | CPDU Index: 1..4
.1.3.6.1.4.1.52964.1.1.50.3.1.2.(1..4).(1..6) | cpduBankIndex | INTEGER | read-only | CPDU Bank Index:1..6
.1.3.6.1.4.1.52964.1.1.50.3.1.3.(1..4).(1..6) | cpduBankName | OCTET STRING | read-only | CPDU Bank Name
.1.3.6.1.4.1.52964.1.1.50.3.1.4.(1..4).(1..6) | cpduBankState | INTEGER | read-only | CPDU Bank State: 0 - Normal 1 - Alarm Min 2 - Alarm Maj
.1.3.6.1.4.1.52964.1.1.50.3.1.5.(1..4).(1..6) | cpduBankVoltage | INTEGER | read-only | CPDU Bank voltage [0.01V]
.1.3.6.1.4.1.52964.1.1.50.3.1.6.(1..4).(1..6) | cpduBankCurrent | INTEGER | read-only | CPDU Bank current [0.01A]
.1.3.6.1.4.1.52964.1.1.50.3.1.7.(1..4).(1..6) | cpduBankActivePower | INTEGER | read-only | CPDU Bank active power [0.1kW]
.1.3.6.1.4.1.52964.1.1.50.3.1.8.(1..4).(1..6) | cpduBankReactivePower | INTEGER | read-only | CPDU Bank reactive power [0.1kVAR] A negative value indicates that the measure value is unavailable.
.1.3.6.1.4.1.52964.1.1.50.3.1.9.(1..4).(1..6) | cpduBankApparentPower | INTEGER | read-only | CPDU Bank apparent power [0.1kVA] A negative value indicates that the measure value is unavailable.
.1.3.6.1.4.1.52964.1.1.50.3.1.10.(1..4).(1..6) | cpduBankActiveEnergy | INTEGER | read-only | CPDU Bank active energy [0.01 kWh] A negative value indicates that the energy value is unavailable.
.1.3.6.1.4.1.52964.1.1.50.4.1.1.(1..4).(1..42) | cpduIndexSockets | INTEGER | read-only | CPDU Index: 1..4
.1.3.6.1.4.1.52964.1.1.50.4.1.2.(1..4).(1..42) | cpduSocketIndex | INTEGER | read-only | CPDU Socket index: 1..42
.1.3.6.1.4.1.52964.1.1.50.4.1.3.(1..4).(1..42) | cpduSocketName | OCTET STRING | read-write | CPDU Socket name
.1.3.6.1.4.1.52964.1.1.50.4.1.4.(1..4).(1..42) | cpduSocketState | INTEGER | read-write | CPDU Socket state: 0 - off 1 - on
.1.3.6.1.4.1.52964.1.1.50.4.1.5.(1..4).(1..42) | cpduSocketVoltage | INTEGER | read-only | CPDU Socket voltage [0.1V]
.1.3.6.1.4.1.52964.1.1.50.4.1.6.(1..4).(1..42) | cpduSocketCurrent | INTEGER | read-only | CPDU Socket current [0.01A]
.1.3.6.1.4.1.52964.1.1.50.4.1.7.(1..4).(1..42) | cpduSocketActivePower | INTEGER | read-only | CPDU Socket active power [0.1kW]
.1.3.6.1.4.1.52964.1.1.50.4.1.8.(1..4).(1..42) | cpduSocketReactivePower | INTEGER | read-only | CPDU Socket reactive power [0.1kVAR] A negative value indicates that the measure value is unavailable.
.1.3.6.1.4.1.52964.1.1.50.4.1.9.(1..4).(1..42) | cpduSocketApparentPower | INTEGER | read-only | CPDU Socket apparent power [0.1kVA] A negative value indicates that the measure value is unavailable.
.1.3.6.1.4.1.52964.1.1.50.4.1.10.(1..4).(1..42) | cpduSocketActiveEnergy | INTEGER | read-only | CPDU Socket active energy [0.01 kWh] A negative value indicates that the measure value is unavailable.
.1.3.6.1.4.1.52964.1.1.100.1.1.0 | lanIp | OCTET STRING | read-write | LAN IP address
.1.3.6.1.4.1.52964.1.1.100.1.2.0 | lanMask | OCTET STRING | read-write | LAN netmask
.1.3.6.1.4.1.52964.1.1.100.1.3.0 | lanGate | OCTET STRING | read-write | LAN Gate
.1.3.6.1.4.1.52964.1.1.100.2.1.0 | securityLevel | INTEGER | read-write | SNMPv3 security Level: 0 - no auth, no priv; 1 - auth, no priv; 2 - auth, priv
.1.3.6.1.4.1.52964.1.1.100.2.2.0 | username | OCTET STRING | read-write | SNMPv3 username
.1.3.6.1.4.1.52964.1.1.100.2.3.0 | authorization | INTEGER | read-write | SNMPv3 authorization algorithm: 0 - SHA1; 1 - MD5
.1.3.6.1.4.1.52964.1.1.100.2.4.0 | authPass | OCTET STRING | read-write | SNMPv3 authorization password
.1.3.6.1.4.1.52964.1.1.100.2.5.0 | privacy | INTEGER | read-write | SNMPv3 privacy algorithm: 0 - AES; 1 - DES
.1.3.6.1.4.1.52964.1.1.100.2.6.0 | privPass | OCTET STRING | read-write | SNMPv3 Privacy password